Number  15	May 10, 1996

Configuring the TI 505 1434TF for the H1 CP1413 DDE Server  by Neal Hatton

This Tech Note issue explains how to configure the Siemens TI 505 1434TF module for use with the Wonderware® Siemens H1 CP1413 DDE Server.  There may be other ways to configure the 1434F module, but the method that is described here is known to work and has been tested by Wonderware Technical Support.

# Procedure

- 1)	Install the Siemens H1 Configurator software on your computer and locate the icons for the configuration software as shown below.  (See the Siemens user documentation for instructions on how to install the H1 Configurator software.)

- 2)	Double click the 505-CP1413TF H1 Configurator icon in the SINEC program group.  The 505-CP1413TF H1 Configurator dialog box should appear as shown here:

- Note the Ethernet address as shown above.  This is the Ethernet address that you want to assign to your PLC.  The address corresponds to the address in the DDE Server Topic.

- 3)	The Wonderware H1 CP1413 DDE Server uses Peer Services.  Therefore, click the Insert button in the 505-CP1413TF H1 Configurator dialog box.  The Peer Service dialog box should appear as shown here:

- Click the Job Button to set the Peer Service as ReadPassive.

- 4)	On the Peer Service dialog box, create the Local TSAP.  Make sure that the ASCII value is set to eight capital F’s (that is, “FFFFFFFF”) and that the Static radio button is selected as shown above.

- 5)	On the same Peer Service dialog box, locate the Remote Ethernet Address field and enter the Ethernet address of the CP1413 card in your computer (example: 00AA0007DEE3).

- 6)	On the same Peer Service dialog box, create the Remote TSAP by making sure the ASCII value is set to two capital W’s (that is, “WW”) as shown above.

- 7)	Click the OK button on the Peer Service dialog box.  Then, click the Insert button again on the 505-CP1413TF H1 Configurator dialog box to create a “WritePassive” Peer Service.  The Peer Service dialog box should appear again as shown here:

- Click the  Job button on the Peer Service dialog box and set the Peer Service to “WritePassive”.

- 8)	On the Peer Service dialog box, create the Local TSAP by making sure that the ASCII value is set to eight capital R’s (that is, “RRRRRRRR”) and that the Static radio button is selected.

- 9)	On the same Peer Service dialog box, locate the Remote Ethernet Address field and enter the Ethernet address of the CP1413 card in your computer.

- 10)	On the same Peer Service dialog box, create the Remote TSAP by making sure the ASCII value is set to two capital W’s (that is, “WW”).

- 11)	Click the OK button on the Peer Service dialog box and select File/Exit from the H1 Configurator software.

- 12)	Start up the H1 CP1413 DDE Server.  Select Configure/Topic from the H1 CP1413 menu.  The H1 CP1413 Topic Configuration dialog box should appear as shown here:

- 13)	Enter the Ethernet address for the PLC.  Make sure that you enter the same address that was displayed in step 2.  Enter “WW” for the Local TSAP, “FFFFFFFF” for the Remote Fetch TSAP, and “RRRRRRRR” for the Remote Receive TSAP.

The Siemens TI 505 1434TF module should now be properly configured to use with the Wonderware Siemens H1 CP1413 DDE Server.  For more information on configuring the H1 CP1413 DDE Server and the Siemens CP1413 communications card, see the Wonderware H1 CP1413 DDE Server User’s Guide or the server’s online help system (select the Help from the server’s main menu).

The Tech Note is published about every two weeks by the Wonderware Technical Support group.  Editor: Mari Fujii;  Technical Publications Coordinator:  Sabrina Haag;  Director of  Technical Support: Sheila S. Tyler;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92718.  E-mail your questions or requests to techpub@wonderware.com.

There is also technical information on the Wonderware software products on the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), and the Comprehensive Support Knowledge Base CD.  Call Wonderware Technical Support at (714) 727-3299 for more information on the BBS, the Wonderware CompuServe forum, or the Comprehensive Support Knowledge Base CD.

Copyright 1996 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

May 10, 1996  Number 15