Number  18	June 17, 1996

Troubleshooting NetDDE Connectivity  by David Ujifusa

Here is a common question that Wonderware Technical Support hears from its users:

“I am trying to get data from another node using NetDDE, but the data is not updating.  What is my problem?”

If this is your situation, then you are having NetDDE connectivity problems.  This Tech Note will provide suggestions that will help you solve most of your NetDDE connectivity problems.  This issue  will cover NetDDE connectivity for Windows (including Windows 3.1, Windows for Workgroups, and Windows 95), Window NT, as well as NetDDE connectivity for VMS (including the VAX and DEC Alpha platforms) and for the UNIX platforms.  The supported network interfaces for the above platforms are NetBIOS, WinSock, DECnet and Serial.

# General NetDDE Troubleshooting Suggestions

Here is a list of general suggestions on troubleshooting NetDDE connectivity problems on all computer platforms and network interfaces:

- 1)	Make sure that NetDDE is running properly on both the local node and the remote destination node.

- 2)	Make sure that the DDE server is running properly on the remote node.

- 3)	See if there are any errors in the error log file.  (On the Windows, Windows NT and Windows 95 platforms, the error log file is the Wonderware Logger (WWLogger).)

- 4)	If you are using the WinSock network interface, then check the following:

- a)	Make sure that you can ping by node name and IP address from the local node to the remote node, and from the remote node to the local node.  If you are not successful, then you need to check your host table.  (Note that the host table has different file names and directory locations, depending on the TCP/IP stack that you are using.  You should consult with your network administrator if you cannot locate the host table.)

- b)	Are you using a TCP/IP stack that is supported by NetDDE? It is possible that other WinSock 1.1 compliant stacks may work under Windows; also other UCX-compliant stacks may work under VMS.

- For a list of the supported TCP/IP stacks, see “Matrix of Supported Network Interfaces” that is on the Wonderware Knowledge Base CD (KBCD).  The KBCD is delivered as part of the Comprehensive Support program.

- c)	For more suggestions on diagnosing NetDDE connectivity problems using the WinSock interface, see Tech Note number 10, “Diagnosing NetDDE WinSock Interface Errors”.

- 5)	Your DDE parameters (that is, the syntax for \\<node>\<application>|<topic>!<item>) may not be correct!  To see if this is the problem, you should test for the following types of connections.

- a)	Test a local connection – Define a DDE connection to your DDE server on the local node without using NetDDE.  In this test, both the DDE client and the DDE server should run on the same computer.

- b)	Test with a different DDE client – Define a NetDDE connection using another DDE client, such as Microsoft Excel or WWClient (which is a utility that is on the KBCD).

- c)	Test with a different DDE server – Connect your DDE client to a different DDE server, such as Excel or Testprot (which is a DDE server utility that is on the KBCD).  Also, connect to a known item, such as “$Second”, in a Wonderware® InTouch™ application.

- 6)	Try running your DDE client or DDE server on a different PC to see if the problem is specific to your PC.

# Windows-Specific NetDDE Troubleshooting Suggestions

Here is a list of suggestions on troubleshooting NetDDE connectivity problems that are specific to Windows and Windows for Workgroups:

Note  If you are running Microsoft Network DDE, then the suggestions in this section will not apply to your situation.  With Network DDE, you can only communicate using the NetBIOS network interface.  Network DDE does not have a front end GUI like Wonderware NetDDE for Windows, so none of the suggestions here will apply.

- 1)	Try the NetDDE menu selections Test/Open Connection and see if it works going to the remote node.  If you are successful, then you will see the connection to the remote node listed in the Internode Connections dialog box.

- 2)	Check your NetDDE configuration.  The following are some common errors to check.  (See the NetDDE online help for more information on each of the following items.)

- a)	Local Node Name.  This is the “Local Node Name” for NetDDE.  Usually this should be set to the default name which is the computer name.

- b)	Network Interfaces.  Make sure that you configure the network interface in which you are trying to communicate.  The “Node Name on Selected Interface” is the network name for that network interface.  It usually should be set to the default value which is the same node name as the “Local Node Name”.  (For the WinSock network interface, the “Node Name on Selected Interface” name must be the TCP/IP Host Name (see the NetDDE online help for exceptions).)

- c)	Preferences.  In most cases, the “Default Route” entry should be left blank.  You should set it to a value only when the local node has to use the same route for all of its connections.

- d)	Routes.  In most cases, the “Routes” entry should be left blank.  You should specify a route only if you will be using two different network interfaces to connect to the destination node.

- e)	Connections.  In most cases, the “Connections” entry should be left blank.  You would specify a connection only if the remote node’s “Node Name on Selected Interface” name is different than the “Local Node Name”.

- 3)	If you are using NetDDE Serial, first make sure you are able to connect the local node to the remote node using the Windows Terminal (See “Frequently Asked Questions on the Serial Interface” in the KBCD for additional NetDDE Serial troubleshooting hints).

# Windows NT-specific Troubleshooting Suggestions

Here is a list of suggestions on troubleshooting NetDDE connectivity problems that are specific to Windows NT:

- 1)	If your DDE server is running on Windows NT, then it needs to have a DDE Trusted Share for the current user that belongs to the Application|Topic for the server.  (See “Configuring Microsoft's NetDDE for Windows NT” in the KBCD on how to configure a DDE Share and “trust” it.)  When you configure the DDE Share, be sure to assign “Everyone” “Full” control in the DDE Share Name Permissions.

- To see which DDE Shares are defined in the DDE Share database, enter the System Registry (that is, execute the REGEDT32.EXE file) and find the entries:

HKEY_LOCAL_MACHINE/Software/Microsoft/NetDDE/DDE Shares

- To see the DDE Trusted Shares for the current user, find the entries:

HKEY_CURRENT_USER/Software/Microsoft/NetDDE/DDE Trusted Shares

- You must have a Trusted Default Share (*|*) or a Trusted Custom Share (this is an explicit application|topic pair) to allow the DDE client to get through the DDE Security to access the DDE server’s application and topic.  Note that when any change is made in a DDE Share, all users using that DDE Share will need to “trust” the DDE Share again.

- 2)	Did you install the Wonderware NetDDE Extensions for Windows NT?  You need to install these extensions only if you want to use NetDDE with TCP/IP or if you need a larger NetDDE message queue size which is required for non-FastDDE communications that has a large volume of DDE traffic.  If you do not need the NetDDE Extensions, then Wonderware Technical Support recommends that you uninstall the extensions (See “Uninstalling NetDDE Extensions for Windows NT” in the KBCD).

- 3)	If you have tried suggestions 1 and 2, but you still cannot get your DDE connection to work, then the NT System Registry may be corrupted.  To solve this problem, you need to reinstall Windows NT on your PC.  (Be sure that you are logged on as an Administrator before you begin to install Windows NT.)

# VMS and UNIX-Specific NetDDE Troubleshooting Suggestions

Here is a list of suggestions on troubleshooting NetDDE connectivity problems that are specific to VMS and the UNIX platforms:

- 1)	Check the NetDDE configuration settings in the NETDDE.INI file which is located in the same directory as the NetDDE executable.  Here are some common errors that you should look for:

- a)	The “Local Node Name” does not match the computer name.  You should correct this by changing the “Local Node Name” so that it is the same as the computer name of your computer.

- b)	The “Network Interface” is not specified.  Make sure that you specify which network interface you will be using (examples: TCP/IP and DECnet).

- c)	“Routes” should be left blank, unless you are using two different network interfaces to connect to the destination node.

- 2)	Look in the error log file, NETDDE.LOG, for any error messages.

- 3)	Test your NetDDE connection with a simple DDE client.  That is, run a DDE client application such as the advise application, which is included with the Wonderware NetDDE SDK for VMS and the NetDDE SDK for UNIX.

- 4)	Test your NetDDE connection with a simple DDE server.  That is, run a DDE server application such as the simpserv application, which is included with the NetDDE SDK for VMS and the NetDDE SDK for UNIX.

- 5)	See if you have more than one copy of NETDDE.INI on your local hard disk.  NetDDE may be using the wrong copy of NETDDE.INI.  The NETDDE.INI file should be in the same directory as the NetDDE executable.

- 6)	Currently, you cannot directly connect a DDE client from a VMS or UNIX node to a DDE server on a Windows NT node using NetDDE.  However, see “Workaround for VMS or UNIX DDE Client to Windows NT DDE Server” on the KBCD for a solution.

- 7)	If you are using DECnet on VMS, then try these commands in the NCP program:

LOOP NODE

LIST KNOWN NODES

SHOW KNOWN NODES.

The Tech Note is published about every two weeks by the Wonderware Technical Support group.  Editor: Mari Fujii;  Technical Publications Coordinator:  Sabrina Haag;  Director of  Technical Support: Sheila S. Tyler;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92718.  E-mail your questions or requests to techpub@wonderware.com.

There is also technical information on the Wonderware software products on the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), and the Comprehensive Support Knowledge Base CD.  Call Wonderware Technical Support at (714) 727-3299 for more information on the BBS, the Wonderware CompuServe forum, or the Comprehensive Support Knowledge Base CD.

Copyright 1996 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

June 17, 1996  Number 18