Number  37	February 4, 1997

Configuring the AB1784KT DDE Server with the 
1784-KTx Card  by Gary Tillery

# Background

The Wonderware® Allen-Bradley 1784-KT DDE I/O Server Release 5.3 and later supports the Allen-Bradley 1784-KTx communication card.  Note that that this release of the AB1784KT DDE Server does require the use of the 1784-KTx firmware on your system.  Though Allen Bradley did not license the firmware to Wonderware, Wonderware Development updated the AB1784KT DDE Server to allow you to use the server with the Allen-Bradley 1784-KTx communication card.

Note  As of the date of this Tech Note, Release 5.3 of the AB1784KT DDE Server is for Windows only.  The Windows NT version of Release 5.3 of the AB1784KT DDE Server will be released shortly.  For more information, contact your local Wonderware distributor.

# Before You Proceed

This Tech Note explains how to set up the AB1784KT DDE Server with the Allen-Bradley 1784-KTx communication card.  Before you proceed to configure the DDE Server, you should have the following on hand:

- 1784-KTx ISA Communication Card Utility Disk: Utility Disk - Diagnostics, Binaries, Release 1.30.

- Note that you may already have the 1784-KTx Binaries (firmware files) in the Allen-Bradley programming software, depending on the version of the programming software that you have.  The binaries or firmware files that you will need are: KTXST0.BIN, KTXST1.BIN, KTXST2.BIN and KTXPCL.BIN.

- Wrist strap.

- This is so you can ground yourself when you install the 1784-KTx communication card.

- 3)	Allen-Bradley 1784-KTx communication card (not the Allen-Bradley 1784-KTxD card).

- Personal computer running Microsoft Windows 3.1, Windows for Workgroups (WFW) 3.11 or 
Windows 95.

# Procedure

Note that the menu options and illustrations shown here are based on the Windows 95 operating system.  The menu options slightly differ for Window and WFW.

## Step 1

Set the 1784-KTx communication card in the computer to a memory base address that is not used by another application program or device card and set the IRQ to none.  Install the 1784-KTx card in the computer.  (If you need more information on how to set the memory base address or the IRQ, please see the Allen Bradley 1784-KTx Communications Interface Card Users Manual.)

## Step 2

Install the Wonderware AB1784KT DDE Server program on the computer.

## Step 3

Start up the AB1784KT DDE Server and maximize the program window.  Select the menus Configure/Adapter Card Settings.  The Adapter Card Settings dialog box should appear as shown here.

Click the New button.  The AB1784KT Adapter Card Settings dialog box should appear as shown on the next page.

Keep the default name Wonder0 for the Card Name.  Select the memory address from the Memory Base Address listbox that you selected for the 1784-KTx communication card in step 1.  Select the Card’s Highway Address from its listbox.  (Make sure that you select a Data Highway node address that is not being used by another adapter card or PLC.)  Keep the remaining settings on the dialog box as shown above.  Select the 1784-Ktx radio button.  Click the Configure button.  The AB1784KT - Firmware Configuration dialog box should appear as shown below.

## Step 4

Select the User Supplied radio button on the AB1784KT - Firmware Configuration dialog box.  The default path for the Firmware File Location is \IPDS\ATTACH\PLC5.  If the 1784-KTx Binaries or firmware files, KTXST0.BIN, KTXST1.BIN, KTXST2.BIN and KTXPCL.BIN, are located in a different directory, then update path in the Firmware File Location listbox.  Click the OK button and also the OK button on the AB1784KT Adapter Card Settings dialog box.

## Step 5

Configure a DDE Topic by selecting the AB1784KT DDE Server menus Configure/Topic Definition and clicking the New button on the Topic Definition dialog box, as shown here:

The AB1784KT Topic Definition dialog box should appear:

Keep the default name “ABPLC” for the Topic Name.  Select “Wonder0” in the Adapter Card Name listbox.  Select the appropriate settings for the PLC Family, Connect Type, Network Addressing and Polling for your PLC configuration.

(In our example here, we chose the PLC-5 for the PLC Family, “Local” for the Connect Type, and a Network Addressing of 1 (which is the PLC 5’s Data Highway node address).  We left the Polling values to their default values.)

When finished, click the OK button, then click the Done button on the Topic Definition dialog box.  Then, minimize the AB1784KT DDE Server program window.

## Step 6

The AB1784KT DDE Server is now ready for you to test.  Start up your Wonderware® InTouch™ application or another client application and advise one or more of the DDE items from the Allen-Bradley PLC.

(As a quick test and one that does not require access to a PLC, Wonderware Technical Support suggests that you use the WWClient utility that is provided on the Wonderware Comprehensive Support Knowledge Base CD (KBCD) to communicate with the AB1784KT DDE Server, or any other Wonderware DDE Server for that matter.  You can quickly locate the WWClient utility on the KBCD by clicking the KBCD Search button and search for “WWClient”.)

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editor: Mari Fujii;  Technical Publications Coordinator: Sabrina Haag;  Director of  Technical Support: Sheila S. Tyler;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

February 4, 1997  Number 37