Number  40                          	 February 24, 1997

Configuring the ABTCP DDE Server under Windows NT 4.0

by Gary Tillery

This Tech Note shows how to configure the Wonderware® Allen-Bradley Ethernet Direct (ABTCP) DDE Server under Microsoft® Windows NT™ 4.0.  Although your system may not be set up exactly as shown here, this example illustrates the starting point for a configuration that will work.

# Installing the TCP/IP Network Protocol

The ABTCP DDE Server requires the TCP/IP network protocol to be able to communicate with a PLC using the WinSock interface.  Follow these steps to install the TCP/IP network protocol, or if you have already installed TCP/IP, then proceed directly to Configuring the ABTCP DDE Server on Page 4 of this Tech Note.

## Step 1

First, double-click the Network icon in the Windows Control Panel.   Then, in the Network dialog box, click the Protocols tab (See Figure 1).  If TCP/IP Protocol is not listed under Network Protocols, then click the Add… button to add the TCP/IP protocol.  You may need to contact your network administrator for an IP address and additional information on adding the TCP/IP protocol for your network.

Figure 1.  The Network dialog box

## Step 2

If you added the TCP/IP protocol, then highlight TCP/IP Protocol listed under Network Protocols in the Network dialog box, and then click the Properties button.  Next, click the IP Address tab in the Microsoft TCP/IP Properties dialog box, and enter the IP Address that your network administrator assigned to the computer that you are working on.  Enter  255.255.255.0 for the Subnet Mask and then enter the IP address again as the Default Gateway.  Then click the Apply button.  In this example, the IP address is 111.111.222.222 (See Figure 2).

Figure 2.  The IP Address Tab in the Microsoft TCP/IP Properties Dialog Box

## Step 3

Click the DNS tab in the Microsoft TCP/IP Properties dialog box and enter the computer’s host name (or node name) and the domain name (or server name).  Then click the Add button and enter the IP address for the domain in DNS Server Search Order, then click the Apply button.   In this example, HOSTS is entered for the host name and GENERIC.COM is entered for the domain name (See Figure 3).

Figure 3.  The DNS Tab in the Microsoft TCP/IP Properties Dialog Box

The TCP/IP network protocol is now properly configured on your computer.  Click the OK button in the Microsoft TCP/IP Properties dialog box.  Then, click the OK button in the Network dialog box.

# Configuring the ABTCP DDE Server

The ABTCP DDE Server can only communicate to a PLC by using the PLC’s host name, not its IP address.  Follow these steps to configure the ABTCP DDE server:

## Step 1

Use a text editor, such as Notepad, to create a new text file called HOSTS.TXT and save the file in the directory \WINDOWS\SYSTEM32\DRIVERS\ETC.  Then, enter the IP address and host name for each PLC that you want to connect to.  In this example, the HOSTS file contains an IP address and host name for one PLC (See Figure 4).

Figure 4.  Sample HOSTS File

The left column lists the IP address of the PLC and the right column lists the corresponding host name.  Remember that your HOSTS file will contain a different IP address and host name than what is shown in this example.

## Step 2

Save the changes in the HOSTS.TXT file and close the text editor.  Then, use the MS-DOS prompt to rename the file to HOSTS, with no file extension.  To rename the file, enter this command at the MS-DOS prompt:

RENAME HOSTS.TXT HOSTS.

Then exit the MS-DOS prompt window by typing EXIT.

Note  Do not rename the file HOSTS.TXT to HOSTS  using Explorer because Explorer will automatically add the file extension .txt to the file HOST.  You can only see that Explorer added this .txt extension if you view the file properties for HOSTS.

## Step 3

Start the ABTCP DDE server and select Configure/Topic Definition from the ABTCP menu.  In the A-B Ethernet Direct Topic Definition dialog box, click the New button to add a new topic (See Figure 5).

Figure 5.  The A-B Ethernet Direct Topic Definition Dialog Box

## Step 4

In the A-B Ethernet Direct Topic Definition dialog box, use the default topic name  (ABPLC) for the DDE Topic Name and choose the appropriate PLC Host Name (ABPLC).   Additional setup parameters are used for this example (See the Wonderware ABTCP DDE Server User’s Guide for information on the remaining options that are in the A-B Ethernet Direct Topic Definition dialog box.).  Click the OK button on the A-B Ethernet Direct Topic Definition dialog box, then exit the ABTCP Server.

# Testing Your Configuration

After you have configured the TCP/IP network protocol and the ABTCP DDE Server, you should test their configuration.   First, open the MS-DOS prompt window, then use the PING utility to “ping” the PLC that you want to communicate with by using its host name.

Note  Make sure that you “ping” the PLC by its host name, and not by its IP address.

## Example 1

This example shows a successful PING operation:

> PING <Node_Name>

Reply From 123.123.123.1

bytes=xx time<xxms TTL = xx  	(This may repeat more than one time.)

Where <Node_Name> is the host name of the PLC, xx is some number, and 123.123.123.123 is the IP address of the PLC.  Note that the format of the PING reply may vary, depending on the PING utility that you use.

## Example 2

This example shows an unsuccessful PING operation:

> PING <Node_Name>

Bad IP Address nodename

This error message could indicate one of the following:

- <Node_Name> was not defined in the HOSTS file;

- the HOSTS file is missing; or

- the HOSTS file is named something other than “HOSTS.”

## Example 3

This example shows another unsuccessful PING operation:

> PING <Node_Name>

Request Timed Out

This error message indicates that <Node_Name> is properly defined in the HOSTS file, but there is a network problem.  You should check for problems in the network cabling, the computer, the PLC, the network terminations, and the network card.

## Completing the Test

If the PING operation was successful, then the ABTCP DDE Server is ready to communicate with the PLC.  To complete the test, find a suitable client, such as Microsoft Excel, InTouch 6.0 or the WWClient utility, to see if you can advise one register (ex. item “S:23” ) from the PLC.

Note   The WWClient utility is available on the Wonderware Knowledge Base CD.   Contact your local Wonderware Distributor for more information on the Knowledge Base CD.

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Technical Publications Coordinator: Sabrina Haag;  Director of  Technical Support: Sheila S. Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

February 24, 1997  Number 40