Number  48	March 14, 1997

Using WWClient to Check DDE Server Communications
by Gary Tillery

# Introduction

WWClient is a generic DDE-aware utility that is provided on Wonderware’s Comprehensive Support Knowledge Base CD (KBCD).  This utility allows you to quickly and easily test a Wonderware® DDE I/O Server configuration.  (WWClient also provides scripting capabilities to automate the process.)  This Tech Note shows how you can use WWClient to test a Wonderware DDE Server’s communications to a PLC device or to troubleshoot a DDE Server by temporarily eliminating communications from specific client applications, such as InTouch.

This Tech Note will show an example that uses the Wonderware® Allen-Bradley Ethernet Direct I/O Server (ABTCP) for Windows NT and the Allen Bradley PLC 5/20E.  The Topic and Items names shown here will vary depending on your DDE Server and PLC.  (For information on how to configure the ABTCP DDE Server, consult the Wonderware User Guide for the ABTCP DDE Server or see the corresponding Tech Notes on the ABTCP DDE Server.)

# Overview of the WWClient Menus

After you install WWClient from the KBCD and start it up, you should see the following WWClient window appear:

Under the DDE menu, WWClient gives you the following menu choices:

INITIATE	Connects to a DDE Server.

TERMINATE	Disconnects from a connected DDE Server.

ADVISE	Creates a DDE Hot Link to topic which will update when the data changes.

UNADVISE	Disconnects and closes an advised Hot Link.

REQUEST	Requests data from a topic only one time (that is, it will not receive any further updated data).

POKE	Sends data to a DDE Server.

EXECUTE	Sends a command to a DDE Server.

Note that if you click the right mouse button anywhere in the WWClient window, it will also display the same DDE functin menu options.

# Installing WWClient

- Start up the KBCD and look for the WWClient by using the KBCD’s Search button.  (WWClient is located under the “Free Applications, Utilities and Add Ons” section.)  The KBCD topic for WWClient will look similar to this:

- Click the CD icon as shown above to install WWClient on your computer.  Specify a destination directory on your hard drive when prompted.  WWClient will then be installed in the directory and ready to use.

# Testing the DDE Server With an Initiate/Advise

Follow these steps to test the DDE Server configuration which will use the WWClient Initiate and Advise commands.

- Start the WWClient utility.  Select Initiate from the DDE menu, as shown here:

- The Initate dialog box should appear:

- 2)	Type the Application name of the DDE Server (example, “abtcp” for the ABTCP DDE Server) and the configured Topic (example, “abplc”).  Click the OK button.

- Note  If the DDE Server is on a remote computer, then you will need to include the nodename of the remote computer in the Node listbox.  Make sure that Wonderware® NetDDE is installed on both the remote node and the local node.

- You should see the established initiated DDE conversation to the DDE Server appear in the WWClient window as shown here:

- If the DDE conversation to the DDE Server does not appear, then the attempted Initiate failed.  This is the same as InTouch issuing the error “Could not Initiate DDE Conversation”.  If WWClient failed to initiate a DDE conversation with the PLC, then you need to check the following:

- Verify that the DDE Server is running properly.

- Verify that the DDE Server’s name is spelled correctly in the Application listbox on the Initiate dialog box.

- Verify that the Topic name was create in the DDE Server or that the Topic name was spelled correctly in the Topic listbox on the Initiate dialog box.

- Once the DDE conversation has successfully initiated, select Advise from the WWClient DDE menu. The Advise dialog box should appear.

- Type the Item name that you wish to Advise (example, S:23 which is the real time in seconds for the Allen Bradley PLC 5/20E).  Click the Advise button, then the Done button.

- You should see the Item updating in the WWClient window as shown here, which indicates that the DDE Server is configured properly:

- If you do not see the Item displayed in the WWClient window, then WWClient will display an error stating that the Advise operation failed.  You should then check the DDE Server configuration, the PLC hardware, cabling, and so on..

# Testing the DDE Server With a Poke

Follow these steps to see if WWClient can successfully Poke a value to an Item in the PLC.

- Follow steps 1 and 2 in “Testing the DDE Server With Initiate/Advise” if you have not yet performed an Initate command In WWClient to the DDE Server.

- Select Poke from the WWClient DDE menu.  The Poke dialog box should appear:

- Type in the Item name to which you wish to Poke a value, along with the actual value.  Click the Poke button, then the Generate button, and then the Done button.

- Confirm that the Poke command was successful by executing the PLC’s programming software and view the data tables in the PLC.

- Or, create another Topic name in the DDE Server and reference the same Item that was advised in “Testing the DDE Server With Initiate/Advise” through the newly created Topic name.  Then Poke the new Topic name.

- For example, here are two different Topics that were Initiated, abplc and abplc2:

- The first Topic, abplc, is advising the Item c5:0.pre which is the Allen-Bradley PLC 5 counter C5:0 preset value.  Then, there is a Poke on this same Item by the second Topic abplc1.  By using this method, you can confirm that the Poke command successfully changed the Item c5:0.pre without having to run the PLC programming software to find out.

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Technical Publications Coordinator: Sabrina Haag;  Director of  Technical Support: Sheila S. Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,  the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.

March 14, 1997  Number 48