Number    78	August 29, 1997

Solving “Could not initiate DDE Conversation” Errors
by Robert Acosta

This Tech Note explains what causes the error “Could not initiate DDE Conversation” when you start up the Wonderware® InTouch™ WindowViewer program and how to resolve the error.    Here is what the error looks like:

Figure 1.    Could Not Initiate DDE Conversation Error

Where “modbus” is the Application/Server Name and “TEST” is the Topic name that’s being used for the DDE Access Name.

There are three causes for this error:

- The I/O Server (or the application that is emulating an I/O Server for the runtime application) has not been started before you started up WindowViewer.

- The DDE Access Name’s DDE Application/Server Name field in the InTouch application does not have the correct executable (.Exe) name.

- The DDE Access Name’s Topic field does not match a defined topic in the I/O Server (or in the application that is emulating an I/O Server for the runtime application).

To resolve the error, first check to see if one of these causes exists (in the order listed above) for your InTouch application.

# Resolving Cause #1

The first cause listed above is the easiest to resolve:    Make sure that the I/O Server is started before you start up WindowViewer.    InTouch is intelligent enough to know that an I/O Server (or an application that is defined in the DDE Application/Server Name field) should be running.    Once you start up the I/O Server, you may click the Start <Application.exe> button on the Initiating DDE Conversation dialog box and InTouch will start the designated application.

## Notes

If the .Exe application does not exist or it has not yet been installed, when you click the Start <Application.exe> button, InTouch will continuously display the Initiating DDE Conversation dialog box.    Simply click the Cancel button to stop displaying the dialog box and install the missing .Exe application.

For Windows, Windows for Workgroups, and Windows 95, if the I/O Server was installed in a directory other than the InTouch directory, the Path statement in the Autoexec.bat file must include the path to the I/O Server directory.    If the I/O Server directory path is omitted, the Initiating DDE Conversation dialog box will appear.

# Resolving Cause #2

The second cause is because the .Exe application name is misspelled in the DDE Application/Server Name field for the DDE Access Name .    Simply correct the .Exe filename in the DDE Application/Server Name field so that it matches the .Exe application that InTouch is expecting to run. Here is an example of an incorrect .Exe filename in the DDE Application/Server Name field in which Modbus is entered as “Mobdus”.

Figure 2 shows the correct spelling of the Modbus application:

Figure 2.    Name of Modbus Application

And figure 3 on the next page shows the misspelled application name that will cause the “Could not initiate DDE conversation” error:    To resolve the error, simply correct the spelling of the application name.

Note    Do not include the path or the file extension, .Exe, with the application name in the DDE Application/Server Name field.    For example, it is incorrect to enter “c:\Intouch32\Modbus.exe” or “Modbus.exe” for the DDE Application/Server Name.    Either entry will cause the “Could not initiate DDE Conversation” error.    The correct entry is simply “Modbus”.

Figure 3.    Misspelled Modbus Application

# Resolving Cause #3

The third cause is because the DDE Topic Name field for the DDE Access Name has an incorrect topic name entered.    The DDE Topic Name field must contain a valid topic name that has been defined in the I/O Server.    Figure 4 shows an example of a DDE Topic Name called “TEST” which must match exactly to the defined topic in the I/O Server.

Figure 4.    Example DDE Topic Name “TEST”

But figure 5 on the next page shows the available topic names in the I/O Server, none of which are named “TEST”.    Because the DDE Topic Name “TEST” does not match an existing topic name in the I/O Server, it will cause the “Could not initiate DDE conversation” error.    To resolve this error, you can either create a new topic in the I/O Server called “TEST” or modify the DDE Access Name in the InTouch application so that the DDE Topic Name matches one of the existing topic names in the I/O Server (that is, “MODBUS”, “PLC1”, or “QUANTUM”).

Figure 5.    Existing I/O Server Topic Names

The Tech Note publication is published periodically by the Wonderware Technical Support group.    Editors: Mari Fujii and Sabrina Haag;    Technical Publications Coordinator: Sabrina Haag;    Director of    Technical Support: Sheila S. Kester;    Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.    E-mail your questions or requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the WonderTech Web site at http://wondertech.wonderware.com, the Wonderware Bulletin Board Service at (714) 727-0726,    the Wonderware CompuServe forum (GO WONDER), the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.    Call Wonderware Technical Support at (714) 727-3299 for more information on the WonderTech Web site, the BBS, the Wonderware CompuServe forum, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1997 Wonderware Corporation.    All Rights Reserved.    Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.                                                                                          August 29, 1997    Number 78