Number  93	February 17, 1998

InControl Quick Reference Guide for the OPTO 22 (AC28) Scanner Card  by Carroll Sparks

This Tech Note details the hardware layout and configuration setup for the OPTO 22 (or AC28) scanner card, which interfaces with the Pamux I/O driver.

# AC28 Scanner Card

The AC28 scanner card is used to link the Pamux I/O bus to any IBM PC/AT or compatible personal computer.  The AC28 scanner card is compatible with computers that feature a standard eight megahertz ISA bus.  Each AC28 scanner card can access up to 512 I/O points.  Up to four AC28 scanner cards can be installed in one PC, which will support up to 2048 I/O points.

Here are the base address jumper settings for the AC28 scanner card:

#### Base Address	Jumper J9	Jumper J8	Jumper J7	Jumper J6

100Hex	In	Out	In	In

140Hex	In	Out	In	Out

180Hex	In	Out	Out	In

280Hex	Out	In	Out	In

And here are the Reset Port Address jumper settings for the AC28 scanner card:

##### Reset Port Address	Jumper R9	Jumper R8

0E0Hex	In	In

1E0Hex	In	Out

2E0Hex	Out	In

3E0Hex	Out	Out

# System Configuration

Run the OPTOPORT utility, which is located under the InControl installation directory (C:\Incontrol), and make sure that the registry settings match the jumper settings on the AC28 scanner card.

When you install the Pamux I/O driver, it will automatically be configured with the following default driver settings for Board 1:

Base Address:	0 100

Base Count:	8

Port Name:	“Pamux”

Card Type:	AC28 Pamux Card

Reset Address:	0 1e0

Reset Count:	1

## Changing the IoPortCount Registry Key

If you will have more than eight racks of I/O, you will need to manually change the IoPortCount key in the Windows registry in order for the Pamux I/O driver to run correctly.  This key is located under:

\HKEY_LOCAL_MACHINE \SYSTEM\ CurrentControlSet \Services \WinRT \WinRTDev0 \Parameters \Section0

After you change the value for the IoPortCount key, exit the registry and reboot the computer in order for the new settings to take effect.

# Cabling

All Pamux stations within a system are daisy-chained via a 50-pin flat ribbon cable.  (Round parallel ribbon cable is not recommended.)  The total cable length cannot exceed 500 feet.

# Configuring Brain Boards B4, B5 and B6

Each Pamux station consists of a brain board and an I/O mounting rack.  The following brain boards can be used:

Brain Board	Capability

B4	Controls up to 32 points of digital I/O

B5	Controls up to 16 points of digital I/O

B6	Controls up to 16 points of analog I/O

## B4 Brain Board

Here are the jumper settings for the base addresses:

##### Base Address	Jumper 4	Jumper 3	Jumper 2	Jumper 1

0	Out	Out	Out	Out

4	Out	Out	Out	In

8	Out	Out	In	Out

12	Out	Out	In	In

16	Out	In	Out	Out

20	Out	In	Out	In

24	Out	In	In	Out

28	Out	In	In	In

32	In	Out	Out	Out

36	In	Out	Out	In

40	In	Out	In	Out

44	In	Out	In	In

48	In	In	Out	Out

52	In	In	Out	In

56	In	In	In	Out

60	In	In	In	In

Here are the jumper settings for the Watchdog timer functions:

Watchdog Timer Function	Jumper 6	Jumper 5

No Action	In	In

Activate relay channel 0 	In	Out

Deactivate all relay channels	Out	In

Activate relay channel 0 and
deactivate relay channels 1-31	Out	Out

And here are the settings for jumper 7 for the reset levels:

Reset Level	Jumper 7

Active High	In

Active Low	Out

Jumper 8 determines how the reset line affects the Watchdog timer function for channel 0.  If jumper 8 is not installed, then the reset line will not affect the watchdog timer function.  However, if jumper 8 is installed and the Watchdog jumpers 5 and 6 are configured to activate channel 0 upon a timeout, then the state of channel 0 depends on if the reset activates before the timeout occurs.  That is:

- If the reset line activates first, then all outputs will deactivate.

- If a timeout occurs first, then the Watchdog function takes place and channel 0 activates.

### Terminate the B4 Station

Both ends of the Pamux I/O bus must be terminated.  To do this, use a Pamux bus terminator board and terminate the last Pamux station.  You can tell if the terminator board is installed correctly making sure that the component side faces away from the I/O modules and its red wire connects to the +5V terminal on the rack.  Note that the AC28 scanner card has a built-in termination capability.

### B4 LED Indicator Lights

Here are the definitions of the B4 LED indicator lights:

LED Indicator	Definition

Select (Address)	ON whenever the Brain board is addressed (that is, read from or written to) on the Pamux I/O bus. Otherwise, it is OFF.

Watchdog	ON if the Pamux I/O bus is idle (that is, no strobe is present) for more than 1.2 seconds.  Otherwise, it is OFF.

## B5 Brain Board

Here are the jumper settings for the base addresses:

## Base Address	Jumper 4	Jumper 3	Jumper 2	Jumper 1	Jumper 0

0	Out	Out	Out	Out	Out

2	Out	Out	Out	Out	In

4	Out	Out	Out	In	Out

6	Out	Out	Out	In	In

8	Out	Out	In	Out	Out

10	Out	Out	In	Out	In

12	Out	Out	In	In	Out

14	Out	Out	In	In	In

16	Out	In	Out	Out	Out

18	Out	In	Out	Out	In

20	Out	In	Out	In	Out

22	Out	In	Out	In	In

24	Out	In	In	Out	Out

26	Out	In	In	Out	In

28	Out	In	In	In	Out

30	Out	In	In	In	In

32	In	Out	Out	Out	Out

34	In	Out	Out	Out	In

36	In	Out	Out	In	Out

38	In	Out	Out	In	In

40	In	Out	In	Out	Out

42	In	Out	In	Out	In

44	In	Out	In	In	Out

46	In	Out	In	In	In

48	In	In	Out	Out	Out

50	In	In	Out	Out	In

52	In	In	Out	In	Out

54	In	In	Out	In	In

56	In	In	In	Out	Out

58	In	In	In	Out	In

60	In	In	In	In	Out

62	In	In	In	In	In

Here are the jumper settings for the Watchdog timer functions:

## Watchdog Function	Jumper 6	Jumper 5

No Action	In	In

Activate relay channel 0	In	Out

Deactivate all relay channels and
activate relay channel 0	Out	In

And deactivate relay channels 1-15	Out	Out

And here are the settings for jumper 7 for the reset levels:

## Reset Level	Jumper 7

Active High	In

Active Low	Out

Jumper 8 determines how the reset line affects the Watchdog timer function for channel 0.  If jumper 8 is not installed, then the reset line will not affect the watchdog timer function.  However, if jumper 8 is installed and the Watchdog jumpers 5 and 6 are configured to activate channel 0 upon a timeout, then the state of channel 0 depends on if the reset activates before the timeout occurs.  That is:

- If the reset line activates first, then all outputs will deactivate.

- If a timeout occurs first, then the Watchdog function takes place and channel 0 activates.

### Terminate the B5 Station

See “Terminate the B4 Station.”

### B5 LED Indicators

See “B4 LED Indicators.”

## B6 Brain Board

Here are the jumper settings for the base addresses:

## Base Address	Jumper 5	Jumper 4	Jumper 3	Jumper 2	Jumper 1

0	Out	Out	Out	Out	Out

2	Out	Out	Out	Out	In

4	Out	Out	Out	In	Out

6	Out	Out	Out	In	In

8	Out	Out	In	Out	Out

10	Out	Out	In	Out	In

12	Out	Out	In	In	Out

14	Out	Out	In	In	In

16	Out	In	Out	Out	Out

18	Out	In	Out	Out	In

20	Out	In	Out	In	Out

22	Out	In	Out	In	In

24	Out	In	In	Out	Out

26	Out	In	In	Out	In

28	Out	In	In	In	Out

30	Out	In	In	In	In

32	In	Out	Out	Out	Out

34	In	Out	Out	Out	In

36	In	Out	Out	In	Out

38	In	Out	Out	In	In

40	In	Out	In	Out	Out

42	In	Out	In	Out	In

44	In	Out	In	In	Out

46	In	Out	In	In	In

48	In	In	Out	Out	Out

50	In	In	Out	Out	In

52	In	In	Out	In	Out

54	In	In	Out	In	In

56	In	In	In	Out	Out

58	In	In	In	Out	In

60	In	In	In	In	Out

62	In	In	In	In	In

- Note  Jumper 6 is not used on the B6 brain board.

Here are the settings for jumper 7 for the reset levels:

## Reset Level	Jumper 7

Active High	In

Active Low	Out

And here are the settings for jumper 8 for the Watchdog timer functions:

## Watchdog	Jumper 8

Disabled	In

Enabled	Out

For more information on the jumper settings for the AC28 scanner card, see the PAMUX User’s Guide.

The Tech Note publication is published periodically by the Wonderware Technical Support group.  Editors: Mari Fujii and Sabrina Haag;  Director of  Technical Support: Sheila Kester;  Publisher, Wonderware Corporation, 100 Technology Drive, Irvine CA 92618.  E-mail your publication questions or topic requests to techpubs@wonderware.com.

There is also technical information on the Wonderware software products on the Technical Services web page at http://www.wonderware.com/support/, the Wonderware Bulletin Board Service at (714) 727-0726, the Comprehensive Support Knowledge Base CD, and the WonderFax FaxBack® service at (714) 450-5050.  Call Wonderware Technical Support at (714) 727-3299 for more information on the Technical Services web page, the BBS, the Comprehensive Support Knowledge Base CD or the WonderFax system.

Copyright 1998 Wonderware Corporation.  All Rights Reserved.  Wonderware is a registered trademark of the Wonderware Corporation in the United States of America and/or other countries.                                           February 17, 1998  Number 93